## Alarm Rationalization
Tag | Alarm Description | Alarm Type | Setpoint | Priority | Probable Cause | Consequence of Inaction | Operator Corrective Action
VT-101 | Incoming line voltage low | LO | < 90% nominal | High | Utility system disturbance or upstream fault | Reduced power quality to entire substation; may cascade to bus undervoltage | Notify utility/system operator; monitor for further degradation or loss of supply
VT-101 | Incoming line voltage high | HI | > 110% nominal | Medium | Utility system disturbance (light load conditions, capacitor switching) | Equipment overvoltage stress | Monitor trend; notify utility operator if sustained
TT-201 | Transformer winding temperature high | HI | > 105°C | Medium | Sustained high loading or cooling system degradation | Accelerated insulation aging; approaching thermal trip | Check transformer loading and cooling fans/radiators; consider load reduction
TT-201 | Transformer winding temperature high-high | HIHI | > 120°C | High | Sustained overload not corrected after HI alarm, or cooling system failure | CB-101 trips automatically (INT-02) to protect the transformer | Confirm trip occurred; do not re-energize until cause is investigated and temperature normalizes
TT-202 | Transformer oil temperature high | HI | > 85°C | Medium | Sustained high loading or cooling system degradation | Accelerated oil degradation; approaching thermal trip | Check cooling system; consider load reduction
TT-202 | Transformer oil temperature high-high | HIHI | > 100°C | High | Sustained overload not corrected after HI alarm | CB-101 trips automatically (INT-02) to protect the transformer | Confirm trip occurred; investigate before re-energizing
VT-301 | Secondary bus voltage low | LO | < 90% nominal | High | Transformer tap position, heavy loading, or incoming voltage sag | Feeder breakers blocked from closing (INT-01); may already be supplying degraded voltage to loads | Check transformer tap setting and incoming voltage; do not attempt to close additional feeders
VT-301 | Secondary bus voltage high | HI | > 110% nominal | Medium | Transformer tap position or light loading conditions | Downstream equipment overvoltage stress | Check transformer tap setting; monitor trend
FT-301 | Bus frequency low | LO | < 59.5 Hz | Medium | Utility system-wide generation/load imbalance | Indicates a wider grid disturbance beyond this substation's control | Monitor trend; this is typically a system-wide condition, not local to this substation
FT-301 | Bus frequency high | HI | > 60.5 Hz | Medium | Utility system-wide generation/load imbalance | Indicates a wider grid disturbance beyond this substation's control | Monitor trend; typically system-wide, not local to this substation
CT-401 | Feeder 1 current high | HI | > 85% of pickup setting | Medium | Feeder approaching its overcurrent protection pickup (normal or developing overload) | Feeder may trip (INT-03) if loading continues to rise | Check feeder loading; consider load shedding/transfer if sustained
CT-402 | Feeder 2 current high | HI | > 85% of pickup setting | Medium | Feeder approaching its overcurrent protection pickup | Feeder may trip (INT-03) if loading continues to rise | Check feeder loading; consider load shedding/transfer if sustained
CT-403 | Feeder 3 current high | HI | > 85% of pickup setting | Medium | Feeder approaching its overcurrent protection pickup | Feeder may trip (INT-03) if loading continues to rise | Check feeder loading; consider load shedding/transfer if sustained
CB-101 | Incoming breaker trip | DI | Trip = True | High | Protection operation (INT-02 thermal or INT-04 instantaneous overcurrent) | Complete loss of supply to the substation | Do not attempt reclose until protection target/cause is identified (INT-05 lockout applies)
CB-201 | Feeder 1 breaker trip | DI | Trip = True | High | Protection operation (INT-03 time-overcurrent) | Loss of supply to Feeder 1 loads | Investigate feeder fault/overload before reset and reclose (INT-05 lockout applies)
CB-202 | Feeder 2 breaker trip | DI | Trip = True | High | Protection operation (INT-03 time-overcurrent) | Loss of supply to Feeder 2 loads | Investigate feeder fault/overload before reset and reclose (INT-05 lockout applies)
CB-203 | Feeder 3 breaker trip | DI | Trip = True | High | Protection operation (INT-03 time-overcurrent) | Loss of supply to Feeder 3 loads | Investigate feeder fault/overload before reset and reclose (INT-05 lockout applies)