Control Narrative

Power Distribution Substation — Incoming Feed, Transformer, and Outgoing Feeders

# 1. Purpose & Scope

This document describes the intended control and protection philosophy for a distribution substation consisting of a single incoming utility feed, a step-down power transformer, and three outgoing distribution feeders. It is the reference document for the accompanying Alarm Rationalization Table and HMI mimic panel.

# 2. Process Description

Utility power arrives via the incoming line, monitored at VT-101 (voltage) and CT-101 (current) and controlled by incoming breaker CB-101. Power passes through step-down transformer T-1 (monitored for winding temperature at TT-201 and oil temperature at TT-202) to the secondary bus, monitored at VT-301 (voltage) and FT-301 (frequency). Three outgoing feeder breakers (CB-201, CB-202, CB-203) distribute power to downstream loads, each with dedicated current monitoring (CT-401/402/403).

# 3. Normal Operating Sequence

## 3.1 Energization

- Confirm no active high-priority alarms and all feeder breakers (CB-201/202/203) open.

- Close CB-101 (incoming breaker) once incoming voltage (VT-101) is confirmed within normal range.

- Monitor transformer temperatures (TT-201, TT-202) and confirm bus voltage (VT-301) establishes within normal band.

- Close feeder breakers (CB-201, CB-202, CB-203) sequentially once bus voltage permissive is satisfied (Section 4).

## 3.2 Normal Running

CB-101 and all feeder breakers remain closed under normal conditions. Feeder currents are monitored continuously against overcurrent protection setpoints; transformer temperatures are monitored continuously against thermal protection setpoints.

## 3.3 De-energization

- Open feeder breakers (CB-201/202/203) first to de-energize downstream loads.

- Open CB-101 (incoming breaker) last.

# 4. Protection Scheme, Interlocks & Permissives

| ID | Protection Function | Description |
| --- | --- | --- |
| INT-01 | 27 — Undervoltage permissive | Feeder breakers (CB-201/202/203) cannot close unless bus voltage (VT-301) is above 90% of nominal |
| INT-02 | 49 — Transformer thermal protection | CB-101 trips if transformer winding temp (TT-201) or oil temp (TT-202) exceeds high-high setpoint |
| INT-03 | 51 — Feeder time-overcurrent | A feeder breaker trips if its current exceeds pickup setpoint for longer than the coordination time delay |
| INT-04 | 50 — Instantaneous overcurrent | CB-101 trips immediately on bus/transformer fault-level current, without time delay |
| INT-05 | 86 — Lockout after trip | Any breaker that trips on protection (INT-02/03/04) is blocked from reclosing until the operator issues a manual reset |
| INT-06 | 81 — Frequency monitoring | Bus frequency (FT-301) outside 59.5–60.5 Hz raises an alarm; no automatic trip is modeled in this simulation |

Protection function numbers follow IEEE C37.2 device number convention, consistent with how these functions would be labeled on real protective relays.

# 5. Alarm Philosophy Summary

Alarms are assigned priority (High / Medium / Low) based on operator response time available and consequence of inaction, consistent with ISA-18.2 principles. Full detail — setpoints, probable cause, and required operator action for every alarm — is maintained in the companion Alarm Rationalization Table (alarm_rationalization.xlsx), not duplicated here.

# 6. References

- IEEE C37.2 — Standard Electrical Power System Device Function Numbers

- ISA-18.2-2016 — Management of Alarm Systems for the Process Industries

- Companion document: alarm_rationalization.xlsx

- Companion system: HMI mimic panel (this project's web application)